## Plant Description
Thermal Power (MW) | 50
Primary Fluid | Helium
Primary Hot Temperature (C) | 630
Primary Cold Temperature (C) | 300
Primary Mass Flow Rate (kg/s)
Primary Pressure (kPa) | 3000
Secondary Fluid | CarbonDioxide
Secondary Hot Temperature (C) | 565
Secondary Cold Temperature (C) | 275
Secondary Mass Flow Rate (kg/s)
Secondary Pressure (kPa) | 25000

## HX Parameters
Plate thickness (m) | 0.001 | Conduction length between primary and secondary channels.
Channel Diameter (m) | 0.001 | Diameter of semi-circular channel. Identical between primary and secondary.
Plate material | SS316
Primary Pressure Drop (kPa) | 50 | Allowable pressure loss in the fluid, currently limited to frictional loss.
Secondary Pressure Drop (kPa) | 50
Step size (m) | 0.005 | Step size in meters for use in steam generator modeling
HX length lower bound (m) | 0.2 | Lower bound of the heat exchanger length search for steam generator modeling
HX length upper bound (m) | 4 | Upper bound of the heat exchanger length search for steam generator modeling

## Cycle Parameters
Pump/Compressor Efficiency | 0.95
Turbine Efficiency | 0.95
Compression Ratio | 3

## Input options
Primary Fluid | Secondary Fluid | Plate Material
Sodium | Air | SS316
Helium | CarbonDioxide | SS304
Organic | Water
Heat pipe